## Aug-24 RT Pk
cid | monitored | dir | ctg | mkt | class | moyr | std | cnt | avg | sum | per_avg | bind% | mon_name | drivers
377193 | AURORA_BROOKNG A | -1 | WHITE-SPLIT ROCK_345 | RT | Peak | 2024-08-01 | 477.58 | 74 | 631.91 | 46761.25 | 132.84 | 21.02% | AURORAWA AURORA_BROOKNG A (LN/WAUE/WAUE) | Steep Bank Lk-Lyons Co-Hawk's Nest Lk 345 kV outages (Brookings Second Circuit project), which forced Buffalo Ridge wind to flow N/S.
455851 | PLESNLEEDS11_1 1 | 1 | BALTA GRE-RAMSEY 230 | RT | Peak | 2024-08-01 | 343.84 | 98 | 318.73 | 31235.67 | 88.74 | 27.84% | PLESNTLK PLESNLEEDS11_1 1 (LN/WAUE/WAUE) | Severe, anomalous derate to 94 MW post-ctg. Summer ratings are typically 120 MW post-ctg.
453296 | GRANIBLAIR23_1 1 | -1 | WATERTOWN - APPLEDORN 230 | RT | Peak | 2024-08-01 | 409.93 | 68 | 261.54 | 17784.67 | 50.52 | 19.32% | GRANITF GRANIBLAIR23_1 1 (LN/WAUE/WAUE) | Steep Bank Lk-Lyons Co-Hawk's Nest Lk 345 kV outages (Brookings Second Circuit project), which forced Buffalo Ridge wind to flow N/S. Big Stone TR outage, Lakefield-Nobles 345 kV outage. Has only bound at summer ratings.
349896 | ASTORIA TR11 | 1 | BROOKINGS COUNTY - ASTORIA 345 | RT | Peak | 2024-08-01 | 118.13 | 95 | 174.97 | 16622.5 | 47.22 | 26.99% | ASTORIA TR1 TR11 (XF/OTP/*) | Big Stone TR, Brookings Second Circuit outages. Wind, coal, gas push.
250872 | NESIGELIOT13_1 1 | -1 | GIBSON-ABBROWN 345 (X15) | RT | Peak | 2024-08-01 | 374.36 | 35 | 410.78 | 14377.25 | 40.84 | 9.94% | NESIGE NESIGELIOT13_1 1 (LN/SIGE/SIGE) | Kaiser Aluminum load, low Culley, Warrick output. Winfield-New Harmony 69 kV outage.
454482 | BOS-NEW2_NIP 1 | -1 | NEW CARLISLE-BOSSERMAN 138 1 | RT | Peak | 2024-08-01 | 780.82 | 15 | 898.87 | 13483.02 | 38.3 | 4.26% | BSMN_NIP BOS-NEW2_NIP 1 (LN/NIPS/AEP) | Babcock-Stillwell, Green Acre-Univ. Park N.-Olive 345 kV outages. Flows reverse direction throughout the day. Strongest forward flows during afternoon load ramp.
285892 | FARGOSHEYN23_1 1 | 1 | BUFFALO - JAMESTOWN 345 | RT | Peak | 2024-08-01 | 172.28 | 71 | 162.11 | 11510.02 | 32.7 | 20.17% | FARGO FARGOSHEYN23_1 1 (LN/WAUE/OTP) | Wind, coal push. Fargo-Moorhead-Morris 230 kV, Prairie-Winger 230 kV, Forman-Forman, Forman-Gwinner 115 kV outages. Only binds at summer ratings.
284960 | WARR-MTGL-3 A | 1 | BELLEAU - MONTGOMERY - 6 345 | RT | Peak | 2024-08-01 | 795.76 | 7 | 1343.71 | 9405.96 | 26.72 | 1.99% | MTGL WARR-MTGL-3 A (LN/AMMO/AMMO) | New Melle, Lake St. Louis, Weldon Spring load. Callaway, Thomas Hill, Iatan push. Sioux, Baldwin relieve.
429792 | STAUTON BK1 | 1 | STAUNTON 230/138 T2 | RT | Peak | 2024-08-01 | 363.1 | 11 | 682.23 | 7504.56 | 21.32 | 3.13% | STAUTON BK1 BK1 (XF/CIN/*) | Dresser-Allendale Jct. Tap-Allendale Jct. 138 kV outage (clean relationship). Cloverdale, Poland, Staunton load. Merom, Jordan Creek Wind Farm, Wabash Valley push.
77127 | RAUNTEKAM16_1 1 | 1 | FORT CALHOUN-RAUN 345 | RT | Peak | 2024-08-01 | 314.88 | 27 | 259.07 | 6994.88 | 19.87 | 7.67% | RAUN RAUNTEKAM16_1 1 (LN/MEC/OPPD) | Southward wind transfer. Supply surplus in the North. Wind generation around Sioux City pushes.
272080 | CREECRES69_1 1 | 1 | CRESTON ALLIANT - SUMMIT LAKE 69 | RT | Peak | 2024-08-01 | 171.7 | 18 | 381.68 | 6870.24 | 19.52 | 5.11% | CREE CREECRES69_1 1 (LN/ALTW/ALTW) | Ottumwa outage. Arispe Tap-Creston-S. Lake 69 kV outages. Creston Solar push. Creston load. Excess MEC gen.
242652 | 5BATES_TALLA 1 | 1 | CHOCTAW-CLAY 500 | RT | Peak | 2024-08-01 | 351.33 | 21 | 294.98 | 6194.65 | 17.6 | 5.97% | 5BATESVI 5BATES_TALLA 1 (LN/TVA/TVA) | Browns Ferry outage. Batesville push (clean relationship), Andrus push. Sardis, Oxford, TVA load.
331256 | WHIG53 2 | 1 | UNIVERSITY - MUKWONAGO 138 (UNIG52 | RT | Peak | 2024-08-01 | 68.98 | 120 | 49.58 | 5949.97 | 16.9 | 34.09% | BLUFFCRK WHIG53 2 (LN/WEC/WEC) | Marine-Rock River 138 kV outage (clean relationship). Whitewater push (clean relationship). Lake Geneva load.
3443 | 13839 A | 1 | WILTON CENTER-DUMONT 765 (11215) | RT | Peak | 2024-08-01 | 130.89 | 47 | 126.58 | 5949.06 | 16.9 | 13.35% | DUNEACRE 13839 A (LN/NIPS/NIPS) | Babcock-Stillwell, Green Acre-Univ. Park N.-Olive 345 kV outages. Flows reverse direction throughout the day. Strongest forward flows during off-pk (evenings). Cook outage.
174626 | SHI_SHW SH | 1 | BLACKHAWK-COLLEY RD 138 (X-54) | RT | Peak | 2024-08-01 | 152.96 | 16 | 369.15 | 5906.36 | 16.78 | 4.55% | SHIRLAND SHI_SHW SH (LN/ALTE/ALTE) | Marine-Rock River 138 kV, Cranston-Rock River 69 kV outages (clean relationship). Riverside, West-Riverside push. Load to the West of Lake Geneva. Darien Solar alleviates some of this now.
197604 | 5061 50 | -1 | ARCADIAN-GRANVILLE 345 (9911) | RT | Peak | 2024-08-01 | 140.12 | 35 | 166.87 | 5840.42 | 16.59 | 9.94% | BLUEMOUN 5061 50 (LN/WEC/WEC) | Summer derate. Cornell-Febrantz 138 kV, Granville-Rangeline 138 kV outages (clear relationship).
457446 | TALLMWEALT13_2 1 | 1 | ROOSEVELT-GAINES 345 | RT | Peak | 2024-08-01 | 464.95 | 8 | 635.15 | 5081.21 | 14.44 | 2.27% | TALLMADG TALLMWEALT13_2 1 (LN/CONS/CONS) | Tallmadge-Wealthy 138 kV parallel circuit outage. Much stronger Pk flows vs. Off-Pk. Ludington push during Pk hours, relieve during Off-Pk hours. Grand Rapids load.
334634 | HILTOP_ST_JOE5 A | -1 | BULL SHOALS-CLE COV-TABLE ROCK 161 | RT | Peak | 2024-08-01 | 370.84 | 9 | 547.75 | 4929.75 | 14 | 2.56% | ST_JOE_E HILTOP_ST_JOE5 A (LN/EAI/EAI) | Stronger Pk flows vs. Off-Pk. Independence, Lake Catherine push. Wolf Creek, Stranger Creek Wind Farm, La Cygne relieve.
281264 | 11335 A | 1 | EUREKA SPRINGS-BEAVER DAM 161 | RT | Peak | 2024-08-01 | 341.15 | 14 | 346.56 | 4851.83 | 13.78 | 3.98% | AUR1241 11335 A (LN/EDE/EDE) | Stronger overnight (Off-Pk) flows. Nixa-Table Rock 161 kV outage. SPP wind, coal pushes.
458149 | ASTORIA TR11 | 1 | ACTUAL | RT | Peak | 2024-08-01 | 410.71 | 11 | 435.58 | 4791.4 | 13.61 | 3.12% | ASTORIA TR1 TR11 (XF/OTP/*) | Big Stone TR, Brookings Second Circuit outages. Wind, coal, gas push.

## Aug-24 RT Off
cid | monitored | dir | ctg | mkt | class | moyr | std | cnt | avg | sum | per_avg | bind% | mon_name | drivers
377193 | AURORA_BROOKNG A | -1 | WHITE-SPLIT ROCK_345 | RT | Off-peak | 2024-08-01 | 401.8 | 46 | 580.99 | 26725.52 | 68.18 | 11.74% | AURORAWA AURORA_BROOKNG A (LN/WAUE/WAUE) | Steep Bank Lk-Lyons Co-Hawk's Nest Lk 345 kV outages (Brookings Second Circuit project), which forced Buffalo Ridge wind to flow N/S.
455851 | PLESNLEEDS11_1 1 | 1 | BALTA GRE-RAMSEY 230 | RT | Off-peak | 2024-08-01 | 464.49 | 62 | 411.78 | 25530.14 | 65.13 | 15.82% | PLESNTLK PLESNLEEDS11_1 1 (LN/WAUE/WAUE) | Severe, anomalous derate to 94 MW post-ctg. Summer ratings are typically 120 MW post-ctg.
281264 | 11335 A | 1 | EUREKA SPRINGS-BEAVER DAM 161 | RT | Off-peak | 2024-08-01 | 287.9 | 33 | 419.63 | 13847.76 | 35.33 | 8.42% | AUR1241 11335 A (LN/EDE/EDE) | Stronger overnight (Off-Pk) flows. Nixa-Table Rock 161 kV outage. SPP wind, coal pushes.
3443 | 13839 A | 1 | WILTON CENTER-DUMONT 765 (11215) | RT | Off-peak | 2024-08-01 | 175.33 | 59 | 169.17 | 9980.75 | 25.46 | 15.05% | DUNEACRE 13839 A (LN/NIPS/NIPS) | Babcock-Stillwell, Green Acre-Univ. Park N.-Olive 345 kV outages. Flows reverse direction throughout the day. Strongest forward flows during off-pk (evenings).
349896 | ASTORIA TR11 | 1 | BROOKINGS COUNTY - ASTORIA 345 | RT | Off-peak | 2024-08-01 | 105.88 | 59 | 145.04 | 8557.39 | 21.83 | 15.05% | ASTORIA TR1 TR11 (XF/OTP/*) | Big Stone TR, Brookings Second Circuit outages. Wind, coal, gas push.
453296 | GRANIBLAIR23_1 1 | -1 | WATERTOWN - APPLEDORN 230 | RT | Off-peak | 2024-08-01 | 157.07 | 56 | 119.06 | 6667.14 | 17.01 | 14.29% | GRANITF GRANIBLAIR23_1 1 (LN/WAUE/WAUE) | Steep Bank Lk-Lyons Co-Hawk's Nest Lk 345 kV outages (Brookings Second Circuit project), which forced Buffalo Ridge wind to flow N/S. Big Stone TR outage, Lakefield-Nobles 345 kV outage. Has only bound at summer ratings.
313988 | MAGICSOURI11_1 1 | 1 | LELAND OLDS-LOGAN_230 | RT | Off-peak | 2024-08-01 | 313.69 | 10 | 397.69 | 3976.9 | 10.15 | 2.55% | MAGIC_CY MAGICSOURI11_1 1 (LN/GRE/GRE) | Weak wind gen in Williston basin. Lack of flows from Estevan, SK, leading to a pull from Border Winds in MB into Rugby. Boundary Dam-Tioga tie line (SPP equipment?) had zero flow. Souris-Minot 115 kV is often taken OOS, preventing this from binding.
367061 | SWAN_WILMA11_1 1 | -1 | SHEAS LAKE - WILMARTH 345 | RT | Off-peak | 2024-08-01 | 171.24 | 17 | 209.42 | 3560.15 | 9.08 | 4.34% | SWAN_LK SWAN_WILMA11_1 1 (LN/NSP/NSP) | Ambient ratings at tightest levels. Wind, gas push. Lakefield-Nobles 345 kV, W. Fairibault-Loon Lake 115 kV, Eagle Lk-Eagle Lk 69 kV outages.
332040 | OVER XFMR_1_345 | 1 | MCCREDIE - OVERTON 345 | RT | Off-peak | 2024-08-01 | 202.12 | 11 | 279 | 3069.04 | 7.83 | 2.81% | OVER X345 XFMR_1_345 (XF/AMMO/*) | Strong wind push from SPP. Thomas Hill outage. Huben-Morgan 345 kV, Hills-Diamond Trail 345 kV outages. Thomas Hill-Mead 161 kV outage. Mid-MO load.
197604 | 5061 50 | -1 | ARCADIAN-GRANVILLE 345 (9911) | RT | Off-peak | 2024-08-01 | 164.82 | 21 | 136.27 | 2861.58 | 7.3 | 5.36% | BLUEMOUN 5061 50 (LN/WEC/WEC) | Summer derate. Cornell-Febrantz 138 kV outage (clear relationship).
454482 | BOS-NEW2_NIP 1 | -1 | NEW CARLISLE-BOSSERMAN 138 1 | RT | Off-peak | 2024-08-01 | 353.55 | 2 | 1416.67 | 2833.33 | 7.23 | 0.51% | BSMN_NIP BOS-NEW2_NIP 1 (LN/NIPS/AEP) | Babcock-Stillwell, Green Acre-Univ. Park N.-Olive 345 kV outages. Flows reverse direction throughout the day. Strongest forward flows during afternoon load ramp. Cook outage.
248380 | S3GRANI11_1 1 | 1 | CEDAR MTN-LYON COUNTY 345 1 (0956) | RT | Off-peak | 2024-08-01 | 61.07 | 21 | 113.08 | 2374.77 | 6.06 | 5.36% | S3 S3GRANI11_1 1 (LN/WAUE/WAUE) | Summer derate. Buffalo Ridge wind push. Hazel Creek-Lyons Co. 345 kV outage.
272080 | CREECRES69_1 1 | 1 | CRESTON ALLIANT - SUMMIT LAKE 69 | RT | Off-peak | 2024-08-01 | 206.13 | 8 | 286.54 | 2292.34 | 5.85 | 2.04% | CREE CREECRES69_1 1 (LN/ALTW/ALTW) | Ottumwa outage. Arispe Tap-Creston-S. Lake 69 kV outages. Creston Solar push. Creston load. Excess MEC gen.
410942 | WHITE_BROOKNGS A | 1 | WATERTOWN-WHITE_345 | RT | Off-peak | 2024-08-01 | 220.93 | 10 | 223.83 | 2238.34 | 5.71 | 2.55% | WHITE WHITE_BROOKNGS A (LN/WAUE/WAUE) | Steep Bank Lk-Lyons Co-Hawk's Nest Lk 345 kV outages (Brookings Second Circuit project), which forced Buffalo Ridge wind to flow N/S.
240392 | WITHYTWINI13_1 1 | 1 | ACTUAL | RT | Off-peak | 2024-08-01 | 303.91 | 3 | 732.63 | 2197.89 | 5.61 | 0.77% | WITHYLKJ WITHYTWINI13_1 1 (LN/CONS/CONS) | Stronger Pk vs. Off-Pk flows, but in the early morning (Off-Pk) of 8/8/24, there was a departure from this pattern. This was when Gallagher-Livingston 345 kV sustained a forced outage.
242652 | 5BATES_TALLA 1 | 1 | CHOCTAW-CLAY 500 | RT | Off-peak | 2024-08-01 | 182.12 | 11 | 176.53 | 1941.81 | 4.95 | 2.8% | 5BATESVI 5BATES_TALLA 1 (LN/TVA/TVA) | Browns Ferry outage. Batesville push (clean relationship), Andrus push. Sardis, Oxford, TVA load.
331256 | WHIG53 2 | 1 | UNIVERSITY - MUKWONAGO 138 (UNIG52 | RT | Off-peak | 2024-08-01 | 41.76 | 40 | 46.77 | 1870.87 | 4.77 | 10.2% | BLUFFCRK WHIG53 2 (LN/WEC/WEC) | Marine-Rock River 138 kV outage (clean relationship). Whitewater push (clean relationship). Lake Geneva load.
396264 | PRES_TIBB_1558 A | 1 | ASTER - COMMODORE 345 (4513) | RT | Off-peak | 2024-08-01 | 143.18 | 18 | 103.69 | 1866.43 | 4.76 | 4.59% | PRES PRES_TIBB_1558 A (LN/AMIL/AMIL) | Coal, wind push. Prairie State Solar push. Steeleville, Sparta load. (Note that the Mount Vernon-W. Frankfort 345 kV outage didn't begin until 9/19/24).
440034 | WATERTN KU1A1 | 1 | WHITE-SPLIT ROCK_345 | RT | Off-peak | 2024-08-01 | 53.2 | 29 | 63.31 | 1835.94 | 4.68 | 7.39% | WATERTN U1A1 KU1A1 (XF/WAUE/*) | Steep Bank Lk-Lyons Co-Hawk's Nest Lk 345 kV outages (Brookings Second Circuit project), which forced Buffalo Ridge wind to flow N/S. Big Stone TR outage.
285892 | FARGOSHEYN23_1 1 | 1 | BUFFALO - JAMESTOWN 345 | RT | Off-peak | 2024-08-01 | 67.73 | 30 | 59.76 | 1792.77 | 4.57 | 7.65% | FARGO FARGOSHEYN23_1 1 (LN/WAUE/OTP) | Wind, coal push. Fargo-Moorhead-Morris 230 kV, Prairie-Winger 230 kV, Forman-Forman, Forman-Gwinner 115 kV outages. Only binds at summer ratings.

## Merged
5BATESVI 5BATES_TALLA 1 (LN/TVA/TVA)
ASTORIA TR1 TR11 (XF/OTP/*)
AUR1241 11335 A (LN/EDE/EDE)
AURORAWA AURORA_BROOKNG A (LN/WAUE/WAUE)
BLUEMOUN 5061 50 (LN/WEC/WEC)
BLUFFCRK WHIG53 2 (LN/WEC/WEC)
BSMN_NIP BOS-NEW2_NIP 1 (LN/NIPS/AEP)
CREE CREECRES69_1 1 (LN/ALTW/ALTW)
DUNEACRE 13839 A (LN/NIPS/NIPS)
FARGO FARGOSHEYN23_1 1 (LN/WAUE/OTP)
GRANITF GRANIBLAIR23_1 1 (LN/WAUE/WAUE)
MAGIC_CY MAGICSOURI11_1 1 (LN/GRE/GRE)
MTGL WARR-MTGL-3 A (LN/AMMO/AMMO)
NESIGE NESIGELIOT13_1 1 (LN/SIGE/SIGE)
OVER X345 XFMR_1_345 (XF/AMMO/*)
PLESNTLK PLESNLEEDS11_1 1 (LN/WAUE/WAUE)
PRES PRES_TIBB_1558 A (LN/AMIL/AMIL)
RAUN RAUNTEKAM16_1 1 (LN/MEC/OPPD)
S3 S3GRANI11_1 1 (LN/WAUE/WAUE)
SHIRLAND SHI_SHW SH (LN/ALTE/ALTE)
ST_JOE_E HILTOP_ST_JOE5 A (LN/EAI/EAI)
STAUTON BK1 BK1 (XF/CIN/*)
SWAN_LK SWAN_WILMA11_1 1 (LN/NSP/NSP)
TALLMADG TALLMWEALT13_2 1 (LN/CONS/CONS)
WATERTN U1A1 KU1A1 (XF/WAUE/*)
WHITE WHITE_BROOKNGS A (LN/WAUE/WAUE)
WITHYLKJ WITHYTWINI13_1 1 (LN/CONS/CONS)