## Sep-24 RT Pk
cid | monitored | dir | ctg | mkt | class | moyr | std | cnt | avg | sum | per_avg | bind% | mon_name | drivers
455851 | PLESNLEEDS11_1 1 | 1 | BALTA GRE-RAMSEY 230 | RT | Peak | 2024-09-01 | 542.31 | 138 | 647.38 | 89338.31 | 279.18 | 43.12% | PLESNTLK PLESNLEEDS11_1 1 (LN/WAUE/WAUE) | Severe, anomalous derate to 94 MW post-ctg. Summer ratings are typically 121 MW post-ctg. Winter ratings of 160 MW begin Nov. 1.
377193 | AURORA_BROOKNG A | -1 | WHITE-SPLIT ROCK_345 | RT | Peak | 2024-09-01 | 445.63 | 55 | 724.29 | 39835.68 | 124.49 | 17.19% | AURORAWA AURORA_BROOKNG A (LN/WAUE/WAUE) | Steep Bank Lk-Lyons Co-Hawk's Nest Lk 345 kV outages (Brookings Second Circuit project), which forced Buffalo Ridge wind to flow N/S.
453296 | GRANIBLAIR23_1 1 | -1 | WATERTOWN - APPLEDORN 230 | RT | Peak | 2024-09-01 | 178.83 | 138 | 282.98 | 39051.27 | 122.04 | 43.13% | GRANITF GRANIBLAIR23_1 1 (LN/WAUE/WAUE) | Steep Bank Lk-Lyons Co-Hawk's Nest Lk 345 kV outages (Brookings Second Circuit project), which forced Buffalo Ridge wind to flow N/S.
207436 | SWAN_WILMA11_1 1 | -1 | HELENA-SHEAS LAKE 345 | RT | Peak | 2024-09-01 | 625.46 | 50 | 582.95 | 29147.46 | 91.09 | 15.63% | SWAN_LK SWAN_WILMA11_1 1 (LN/NSP/NSP) | Brookings Second Circuit project increased binding risk, but this wasn't the solitary driver. Northern IA wind, Mankato Energy Center push are necessary for binding events.
77127 | RAUNTEKAM16_1 1 | 1 | FORT CALHOUN-RAUN 345 | RT | Peak | 2024-09-01 | 586.7 | 33 | 557.61 | 18401 | 57.5 | 10.31% | RAUN RAUNTEKAM16_1 1 (LN/MEC/OPPD) | Southward wind transfer. Supply surplus in the North. Wind generation around Sioux City pushes. Sensitive to SPP push. Tekamah-Oakland 161 kV outages can slightly fatten the tails of the constraint flow distribution.
280856 | MONRONSTAR12_1 1 | 1 | MOROCCO-MONROE-MILAN 345 | RT | Peak | 2024-09-01 | 206.9 | 67 | 258.03 | 17288.3 | 54.03 | 20.94% | MONROE4 MONRONSTAR12_1 1 (LN/DECO/DECO) | Coventry-Monroe 345 kV outage. This is interesting, as the outage ticket mentioned that Monroe Units 3 & 4 would be limited to 1,100 MVA specifically to prevent contingent overloads on this constraint. Yet, the two units still ran at 700-1,400 MW (flexing up/down during pk/off-pk) throughout the 9/14-9/20 binding event! The relationship is clean.
459833 | X-53 3 | 1 | ACTUAL | RT | Peak | 2024-09-01 | 301.27 | 46 | 374.46 | 17225.34 | 53.83 | 14.38% | PADDOCK X-53 3 (LN/ALTE/ALTE) | Big Hill Park-Townline 138 kV, Bass Ck-Townline 138 kV outages. Kittyhawk-Townline 138 kV outages. Summer ratings (246 MW) last until Oct. 1. Intermediate ratings (274 MW) last from Oct. 1-Nov. 1. Winter ratings are 292 MW.
284948 | FORBEARROW23_1 1 | 1 | ARROWHEAD-HILLTOP-IRON RANGE 230 | RT | Peak | 2024-09-01 | 174.21 | 131 | 126.97 | 16633.01 | 51.98 | 40.94% | FORBES FORBEARROW23_1 1 (LN/MP/MP) | Rush-Red Rock 345 kV outage, Rock Ck-Red Rock 230 kV outage, Linwood-Red Rock 230 kV outage, Eau Claire-King 345 kV outage, 16L Tap-Cotton 115 kV outage. Constraint flows show some seasonality, peaking in the summer.
396264 | PRES_TIBB_1558 A | 1 | ASTER - COMMODORE 345 (4513) | RT | Peak | 2024-09-01 | 288.29 | 65 | 233.84 | 15199.36 | 47.5 | 20.31% | PRES PRES_TIBB_1558 A (LN/AMIL/AMIL) | Mt. Vernon-W. Frankfort E. 345 kV outage, Lutesville-St. Francis 345 kV outage. Coal push (Baldwin, Prairie State, Labadie).
314718 | FORMAFORMN11_1 1 | 1 | HANKINSON-WAHPETON 230+WAHPETN TR2 | RT | Peak | 2024-09-01 | 169.07 | 84 | 162.23 | 13627.56 | 42.59 | 26.25% | FORMAN FORMAFORMN11_1 1 (LN/OTP/WAUE) | Summer ratings (125 MW post-contingent) persist until beginning of November. Forman-Gwinner 115 kV outage. Eastward wind transfer.
270260 | MAPLE08CHR13_1 1 | 1 | HIGHLAND PARK-NEW LONDON 230 23009 | RT | Peak | 2024-09-01 | 566.92 | 13 | 670.57 | 8717.35 | 27.24 | 4.06% | MAPLE MAPLE08CHR13_1 1 (LN/CIN/CIN) | Ambient ratings were near minimum values. Some 69 kV outages near Kokomo were mildly bullish (which is consistent with our Kokomo-Tipton experience). Noblesville outage. Nuclear push is worth noting.
429204 | MARS_SARAT11_1 1 | 1 | MARS SE-MARS SW_115 | RT | Peak | 2024-09-01 | 129.97 | 52 | 149.28 | 7762.55 | 24.26 | 16.25% | MARS_SW MARS_SARAT11_1 1 (LN/NSP/NSP) | Lyons Co-Marshall 115 kV outage, Brookings Second Circuit project. Wind push. Lyons Co-Marshall plus strong wind in the Buffalo Ridge region could be sufficient to force a binding event, even after the Brookings Second Circuit project.
348158 | HS_EHV_BUTERF3 A | -1 | SHERIDAN - MAGNET COVE 500 | RT | Peak | 2024-09-01 | 207.95 | 30 | 253.72 | 7611.51 | 23.79 | 9.38% | BUTERF HS_EHV_BUTERF3 A (LN/EAI/EAI) | Sheridan-El Dorado 500 kV outage exacerbated gas push. Akansas Nuclear One derate was moderately bullish too.
378621 | CLAY_PRAIRIE 1 | 1 | BROWNS FERRY - WEST POINT 500 | RT | Peak | 2024-09-01 | 587.03 | 5 | 1485.39 | 7426.94 | 23.21 | 1.56% | 8CLAY_MS CLAY_PRAIRIE 1 (LN/TVA/TVA) | SOCO generation pushes, TVA load pulls. Sheridan-El Dorado 500 kV outage.
347842 | BRIGGSRD TR9_2 | -1 | ACTUAL | RT | Peak | 2024-09-01 | 611.94 | 8 | 872.64 | 6981.08 | 21.82 | 2.5% | BRIGGSRD R9_2 TR9_2 (XF/NSP/*) | Eau Claire-King 345 kV outage, Chester-Rochester 161 kV outage. John P Madgett outage.
4862 | K-11_2 2 | -1 | MANRAP-SHOTO 69 (C-55) | RT | Peak | 2024-09-01 | 158.94 | 61 | 96.61 | 5893.03 | 18.42 | 19.07% | NEAST K-11_2 2 (LN/WPS/WPS) | Point Beach Solar, Two Creeks Solar push. Manitowoc load. Lakefront (SSR) is on the high side. Only attractive during summer ratings Pk.
460264 | 6902B 2 | 1 | SYCAMORE 138/69 T4 | RT | Peak | 2024-09-01 | 600.93 | 8 | 731.5 | 5851.97 | 18.29 | 2.5% | GATEWAY 6902B 2 (LN/MGE/MGE) | Femrite XF 138/69 kV outage. Sycamore XF 138/69 kV outage. Uprated 1/11/25 from 81 MW to 218 MW. I don't see this binding ever again baring truly exceptional topological disasters.
313988 | MAGICSOURI11_1 1 | 1 | LELAND OLDS-LOGAN_230 | RT | Peak | 2024-09-01 | 571.22 | 11 | 412.59 | 4538.47 | 14.18 | 3.44% | MAGIC_CY MAGICSOURI11_1 1 (LN/GRE/GRE) | Summer ratings Weak wind NE of the Williston basin. Lack of imports from Estevan, SK.
334600 | HETINCENTP11_1 1 | 1 | BOWMAN-HETTINGER_230 | RT | Peak | 2024-09-01 | 73.52 | 52 | 86.04 | 4474.09 | 13.98 | 16.25% | HETINGR HETINCENTP11_1 1 (LN/MDU/MDU) | Requires Northward flows on Maurine-Bison 230 kV to bind. Oahe-Philip Tap, Oahe-Sully Buttes, Oahe-Ft. Thompson 230 kV outages increased sensitivitypush from the South. $250k of M2M settlements paid from MISO to SPP indicate that MISO's ratings were too low. 9/25, 9/28, 9/30 (as well as 4 days in Oct-24 and 3 days in Dec-24) warranted settlements. That is, there would have been more MISO congestion than there was had MISO had the correct ratings.
296436 | CHAR_WATFO23_1 1 | 1 | CHARLIE CREEK - PATENT GATE 345 | RT | Peak | 2024-09-01 | 407.85 | 13 | 336.16 | 4370.08 | 13.66 | 4.06% | CHAR_CK CHAR_WATFO23_1 1 (LN/WAUE/WAUE) | L11 - Mocassin 115 kV outage. Summer ratings. Antelope pushes. Lonesome Creek relieves.

## Sep-24 RT Off
cid | monitored | dir | ctg | mkt | class | moyr | std | cnt | avg | sum | per_avg | bind% | mon_name | drivers
453296 | GRANIBLAIR23_1 1 | -1 | WATERTOWN - APPLEDORN 230 | RT | Off-peak | 2024-09-01 | 120.71 | 163 | 202.2 | 32958.91 | 82.4 | 40.75% | GRANITF GRANIBLAIR23_1 1 (LN/WAUE/WAUE) | Steep Bank Lk-Lyons Co-Hawk's Nest Lk 345 kV outages (Brookings Second Circuit project), which forced Buffalo Ridge wind to flow N/S.
455851 | PLESNLEEDS11_1 1 | 1 | BALTA GRE-RAMSEY 230 | RT | Off-peak | 2024-09-01 | 337.52 | 79 | 352.42 | 27841.43 | 69.6 | 19.75% | PLESNTLK PLESNLEEDS11_1 1 (LN/WAUE/WAUE) | Severe, anomalous derate to 94 MW post-ctg. Summer ratings are typically 121 MW post-ctg. Winter ratings of 160 MW begin Nov. 1.
377193 | AURORA_BROOKNG A | -1 | WHITE-SPLIT ROCK_345 | RT | Off-peak | 2024-09-01 | 373.01 | 35 | 531.74 | 18610.96 | 46.53 | 8.75% | AURORAWA AURORA_BROOKNG A (LN/WAUE/WAUE) | Steep Bank Lk-Lyons Co-Hawk's Nest Lk 345 kV outages (Brookings Second Circuit project), which forced Buffalo Ridge wind to flow N/S.
207436 | SWAN_WILMA11_1 1 | -1 | HELENA-SHEAS LAKE 345 | RT | Off-peak | 2024-09-01 | 346.73 | 50 | 347.34 | 17366.94 | 43.42 | 12.5% | SWAN_LK SWAN_WILMA11_1 1 (LN/NSP/NSP) | Brookings Second Circuit project increased binding risk, but this wasn't the solitary driver. Northern IA wind, Mankato Energy Center push are necessary for binding events.
332040 | OVER XFMR_1_345 | 1 | MCCREDIE - OVERTON 345 | RT | Off-peak | 2024-09-01 | 176.69 | 73 | 184.03 | 13433.85 | 33.58 | 18.25% | OVER X345 XFMR_1_345 (XF/AMMO/*) | Wind push, coal push. At risk of binding whenever Eastward flows across MO are material.
1531 | TEKAMSUB1216_1 1 | 1 | FORT CALHOUN-RAUN 345 | RT | Off-peak | 2024-09-01 | 243.21 | 56 | 239.36 | 13404.05 | 33.51 | 14% | TEKAMHO TEKAMSUB1216_1 1 (LN/OPPD/OPPD) | Southward wind transfer. IA, NE, Buffalo Ridge area wind push. Omaha pull.
347842 | BRIGGSRD TR9_2 | -1 | ACTUAL | RT | Off-peak | 2024-09-01 | 1195.88 | 9 | 1355.69 | 12201.18 | 30.5 | 2.25% | BRIGGSRD R9_2 TR9_2 (XF/NSP/*) | Eau Claire-King 345 kV outage, Chester-Rochester 161 kV outage. John P Madgett outage.
314718 | FORMAFORMN11_1 1 | 1 | HANKINSON-WAHPETON 230+WAHPETN TR2 | RT | Off-peak | 2024-09-01 | 139.81 | 72 | 161.42 | 11621.89 | 29.05 | 18% | FORMAN FORMAFORMN11_1 1 (LN/OTP/WAUE) | Summer ratings (125 MW post-contingent) persist until beginning of November. Forman-Gwinner 115 kV outage. Eastward wind transfer.
396264 | PRES_TIBB_1558 A | 1 | ASTER - COMMODORE 345 (4513) | RT | Off-peak | 2024-09-01 | 178.13 | 93 | 116.46 | 10830.47 | 27.08 | 23.25% | PRES PRES_TIBB_1558 A (LN/AMIL/AMIL) | Mt. Vernon-W. Frankfort E. 345 kV outage, Lutesville-St. Francis 345 kV outage. Coal push (Baldwin, Prairie State, Labadie).
77127 | RAUNTEKAM16_1 1 | 1 | FORT CALHOUN-RAUN 345 | RT | Off-peak | 2024-09-01 | 245.55 | 40 | 228.64 | 9145.48 | 22.86 | 10% | RAUN RAUNTEKAM16_1 1 (LN/MEC/OPPD) | Southward wind transfer. Supply surplus in the North. Wind generation around Sioux City pushes. Sensitive to SPP push. Tekamah-Oakland 161 kV outages can slightly fatten the tails of the constraint flow distribution.
413238 | BNCRTBURTM69_1 1 | -1 | BURT - OSGOOD 161 | RT | Off-peak | 2024-09-01 | 527.25 | 8 | 1039.93 | 8319.47 | 20.8 | 2% | BNCRT BNCRTBURTM69_1 1 (LN/WAUE/WAUE) | Local wind drought near Bancroft, Estherville, Sprit Lake, IA.
231008 | KNOXVLUCAS69_1 1 | 1 | BONDURANT - MONTEZUMA 345 | RT | Off-peak | 2024-09-01 | 149.34 | 27 | 294.58 | 7953.76 | 19.88 | 6.75% | KNOXVIL KNOXVLUCAS69_1 1 (LN/MEC/ALTW) | Knoxville-Knoxville 69 kV outage increased sensitivity to wind push, fattening the tails of the constraint flow distribution.
278994 | W_KEOROQUE69_1 1 | -1 | E. QUINCY - HAMILTON 138 | RT | Off-peak | 2024-09-01 | 484.17 | 20 | 384.01 | 7680.2 | 19.2 | 5% | W_KEOKUK W_KEOROQUE69_1 1 (LN/ALTW/ALTW) | Keokuk push. The new Keokuk-Carbide 69 kV, Keokuk--Geode 69 kV lines came online 5/14/25. This marks a clear change-point in the constraint flow time series, substantially decreasing binding risk. Both summer ratings and strong Keokuk push were necessary for this to bind.
280856 | MONRONSTAR12_1 1 | 1 | MOROCCO-MONROE-MILAN 345 | RT | Off-peak | 2024-09-01 | 206.89 | 27 | 279.68 | 7551.29 | 18.88 | 6.75% | MONROE4 MONRONSTAR12_1 1 (LN/DECO/DECO) | Coventry-Monroe 345 kV outage. This is interesting, as the outage ticket mentioned that Monroe Units 3 & 4 would be limited to 1,100 MVA specifically to prevent contingent overloads on this constraint. Yet, the two units still ran at 700-1,400 MW (flexing up/down during pk/off-pk) throughout the 9/14-9/20 binding event! The relationship is clean.
334600 | HETINCENTP11_1 1 | 1 | BOWMAN-HETTINGER_230 | RT | Off-peak | 2024-09-01 | 249.05 | 53 | 132.17 | 7004.78 | 17.51 | 13.25% | HETINGR HETINCENTP11_1 1 (LN/MDU/MDU) | Requires Northward flows on Maurine-Bison 230 kV to bind. Oahe-Philip Tap, Oahe-Sully Buttes, Oahe-Ft. Thompson 230 kV outages increased sensitivitypush from the South. $250k of M2M settlements paid from MISO to SPP indicate that MISO's ratings were too low. 9/25, 9/28, 9/30 (as well as 4 days in Oct-24 and 3 days in Dec-24) warranted settlements. That is, there would have been more MISO congestion than there was had MISO had the correct ratings.
296436 | CHAR_WATFO23_1 1 | 1 | CHARLIE CREEK - PATENT GATE 345 | RT | Off-peak | 2024-09-01 | 466.96 | 17 | 405.44 | 6892.5 | 17.23 | 4.25% | CHAR_CK CHAR_WATFO23_1 1 (LN/WAUE/WAUE) | L11 - Mocassin 115 kV outage. Summer ratings. Antelope pushes. Lonesome Creek relieves.
429204 | MARS_SARAT11_1 1 | 1 | MARS SE-MARS SW_115 | RT | Off-peak | 2024-09-01 | 68.56 | 39 | 167.2 | 6520.66 | 16.3 | 9.75% | MARS_SW MARS_SARAT11_1 1 (LN/NSP/NSP) | Lyons Co-Marshall 115 kV outage, Brookings Second Circuit project. Wind push. Lyons Co-Marshall plus strong wind in the Buffalo Ridge region could be sufficient to force a binding event, even after the Brookings Second Circuit project.
281264 | 11335 A | 1 | EUREKA SPRINGS-BEAVER DAM 161 | RT | Off-peak | 2024-09-01 | 221.31 | 19 | 342.63 | 6509.95 | 16.27 | 4.75% | AUR1241 11335 A (LN/EDE/EDE) | Sensitive to SPP wind and coal generation. Nixa-Table Rock 161 kV outage.
306996 | GRINNSGRIN69_1 1 | 1 | BONDURANT - MONTEZUMA 345 | RT | Off-peak | 2024-09-01 | 547.12 | 13 | 498.75 | 6483.78 | 16.21 | 3.25% | GRINNEL GRINNSGRIN69_1 1 (LN/ALTW/ALTW) | Powesheik Co-Reasnor 161 kV, Powesheik Co-Irvine 161 kV outages (clean relationship).
375350 | EXSPRNG_CARR A | 1 | OVERTON - SIBLEY - 3 345 | RT | Off-peak | 2024-09-01 | 311.62 | 18 | 354.59 | 6382.67 | 15.96 | 4.5% | MAUR_HS EXSPRNG_CARR A (LN/KCPL/KCPL) | SPP wind transfer. Thomas Hill outage on the high side.