## Oct-24 RT Pk
cid | monitored | dir | ctg | mkt | class | moyr | std | cnt | avg | sum | per_avg | bind% | mon_name | drivers | notes
350280 | OAHESULLY23_1 1 | 1 | LELAND OLDS - CHAPELLE CREEK 345 | RT | Peak | 2024-10-01 | 421.72 | 83 | 540.59 | 44868.63 | 121.93 | 22.55% | OAHE OAHESULLY23_1 1 (LN/WAUE/WAUE) | Ft. Thompson-Oahe Dam Ckt 2 230 kV outage (case outage -- no corresponding ticket!). Excess MDU load. Week MDU wind generation. Summer ratings.
314718 | FORMAFORMN11_1 1 | 1 | HANKINSON-WAHPETON 230+WAHPETN TR2 | RT | Peak | 2024-10-01 | 281.24 | 105 | 386.65 | 40597.89 | 110.32 | 28.53% | FORMAN FORMAFORMN11_1 1 (LN/OTP/WAUE) | Summer ratings. Eastward wind transfer from MISO into SPP. Lisbon-Enderlin 69 kV outage. | Winter ratings from 11/1-4/1. Winter (only) B-ratings uprated from 131 MW to 169 MW in Winter 2024-25.
77127 | RAUNTEKAM16_1 1 | 1 | FORT CALHOUN-RAUN 345 | RT | Peak | 2024-10-01 | 309.93 | 103 | 352.5 | 36307.45 | 98.66 | 27.99% | RAUN RAUNTEKAM16_1 1 (LN/MEC/OPPD) | Southward wind transfer from the greater Sioux City, IA area (including SPP) into Omaha, NE. Flows show a strong negative correlation with Walter Scott Jr. output. | Curious B-rating uprate on 11/8/2024 from 217 MW to 284 MW. This was followed by a 1/30/2025 B-rating derate from 284 MW to 259 MW then again on 2/21/2025 from 259 MW to 256 MW and again on 4/7/2025 from 256 MW to 217 MW. Tekamah-Oakland 115 kV is a switching solution that relieves Tekamah-Substation 1226 at the expense of increasing flows on Raun-Tekamah.
455851 | PLESNLEEDS11_1 1 | 1 | BALTA GRE-RAMSEY 230 | RT | Peak | 2024-10-01 | 271.27 | 75 | 364.42 | 27331.45 | 74.27 | 20.38% | PLESNTLK PLESNLEEDS11_1 1 (LN/WAUE/WAUE) | Severe, unprecedented derate. Clean relationship between binding events and the derate. Hasn't bound since.
396264 | PRES_TIBB_1558 A | 1 | ASTER - COMMODORE 345 (4513) | RT | Peak | 2024-10-01 | 140.36 | 167 | 127.59 | 21307.62 | 57.9 | 45.38% | PRES PRES_TIBB_1558 A (LN/AMIL/AMIL) | Mt. Vernon-W. Frankfort 230 kV outage. Moderate sum of wind generation and coal generation. Load to the South, Southeast.
296436 | CHAR_WATFO23_1 1 | 1 | CHARLIE CREEK - PATENT GATE 345 | RT | Peak | 2024-10-01 | 492.01 | 32 | 527.02 | 16864.67 | 45.83 | 8.7% | CHAR_CK CHAR_WATFO23_1 1 (LN/WAUE/WAUE) | Bound often before 12/17/2024. A clear regime change occurred on 12/18/2024 which drastically reduced post-contingent flow.
306800 | GRINNSGRIN69_1 1 | 1 | OTTUMWA - MONTEZUMA 345 | RT | Peak | 2024-10-01 | 582.84 | 15 | 773.29 | 11599.36 | 31.52 | 4.08% | GRINNEL GRINNSGRIN69_1 1 (LN/ALTW/ALTW) | Diamond Trail-Hills 345 kV, Powesheik Co-Reasnor 161 kV outages. Wind push.
464020 | MORRIS KV1A1 | 1 | CANBY-DAWSON-LOUISBURG-APPLETN 115 | RT | Peak | 2024-10-01 | 518.85 | 15 | 729.28 | 10939.2 | 29.73 | 4.08% | MORRIS V1A1 KV1A1 (XF/WAUE/*) | Big Stone TR 230/115 kV, Benson-Swenoda 115 kV outages increased binding likelihood.
235516 | SCRIBWILTO11_1 1 | -1 | WILTON-WINGER_230 | RT | Peak | 2024-10-01 | 661.1 | 12 | 624.34 | 7492.13 | 20.36 | 3.26% | SCRIBNER SCRIBWILTO11_1 1 (LN/OTP/OTP) | Weak wind in OTP and high Boswell generation.
375865 | NEVADFERNA69_1 1 | -1 | STORY CO-MARSHALTOWN WEST MAIN 161 | RT | Peak | 2024-10-01 | 68.03 | 47 | 150.08 | 7053.88 | 19.17 | 12.77% | NEVADATP NEVADFERNA69_1 1 (LN/ALTW/ALTW) | Doud-Boone Junction 161 kV, Karma-Perry 161 kV outages. Story County, Great Pathfinder wind generation.
349896 | ASTORIA TR11 | 1 | BROOKINGS COUNTY - ASTORIA 345 | RT | Peak | 2024-10-01 | 149.4 | 37 | 190.15 | 7035.46 | 19.12 | 10.06% | ASTORIA TR1 TR11 (XF/OTP/*) | Big Stone TR 230/115 kV, Big Stone-Brownsville 230 kV outages. High sensitivity to wind push at Dakota Range, Crowned Ridge, Deuel Harvest, etc. Clean relationship with Big Stone TR outage.
295416 | WPRISN_WIN1153 A | 1 | LAYFIELD - CAROLL 230 | RT | Peak | 2024-10-01 | 781.72 | 6 | 1167.05 | 7002.29 | 19.03 | 1.63% | WIN115 WPRISN_WIN1153 A (LN/EES/EES) | Sarepta-Longwood 345 kV outage. ERCOT East DC tie line "load."
374541 | RLNDFERNA69_1 1 | -1 | STORY CO-MARSHALTOWN WEST MAIN 161 | RT | Peak | 2024-10-01 | 428.05 | 13 | 512.62 | 6664.03 | 18.11 | 3.53% | RLND RLNDFERNA69_1 1 (LN/WAUE/ALTW) | Doud-Boone Junction 161 kV, Karma-Perry 161 kV outages. Story County, Great Pathfinder wind generation.
465155 | SHADELAFAY13_1 1 | 1 | 08NW TAP - W AIRPORT - PURDUE 138 | RT | Peak | 2024-10-01 | 194.32 | 9 | 738.36 | 6645.24 | 18.06 | 2.45% | SHADELND SHADELAFAY13_1 1 (LN/CIN/CIN) | Monticello-Lafayette-Lafayette LC 138 kV outages. | Bound briefly before substantial uprate on 10/29/2025 from 198 MW to 357 MW (post-contingent). Unlikely to bind in the current regime.
3336 | ROCK_DEWIT16_1 1 | 1 | QUAD CITIES-SUB 91 345 + SUB 91 XF | RT | Peak | 2024-10-01 | 243.02 | 23 | 278.98 | 6416.5 | 17.44 | 6.25% | ROCK_CK ROCK_DEWIT16_1 1 (LN/ALTW/ALTW) | Cordova-Substation 39 345 kV outage. Quad Cities push.
465036 | RINGOL_SAILES3 A | -1 | LAYFIELD - CAROLL 230 | RT | Peak | 2024-10-01 | 326.99 | 12 | 524.57 | 6294.87 | 17.11 | 3.26% | RINGOL RINGOL_SAILES3 A (LN/EES/EES) | Sarepta-Longwood 345 kV outage. Weak Harrison County generation. Weak OK wind generation.
62613 | LUANPOSTV69_1 1 | -1 | LANSING-POSTVILLE 161 | RT | Peak | 2024-10-01 | 147.97 | 27 | 230.81 | 6231.82 | 16.93 | 7.34% | LUAN LUANPOSTV69_1 1 (LN/ALTW/DPC) | Harmony-Lansing 161 kV outage. | This is odd, as it looks like the monitored element is radial. I'm not fully sure what's going on here.
324540 | LIME_BARTO16_1 1 | 1 | KILLDEER - QUINN 345 | RT | Peak | 2024-10-01 | 66.66 | 88 | 68 | 5983.89 | 16.26 | 23.91% | LIME_CK LIME_BARTO16_1 1 (LN/ALTW/ALTW) | Floyd-Emery-Sheffield, Worth Co-Glenville-Hayward 161 kV outages. Wind generation in Northern IA.
349600 | WOODYAPANO16_1 2 | 1 | OTTUMWA - HUGH 345 | RT | Peak | 2024-10-01 | 185.45 | 28 | 212.06 | 5937.59 | 16.13 | 7.61% | WOODY WOODYAPANO16_1 2 (LN/ALTW/ALTW) | Southward wind transfer from IA into MO. Hills-Diamond Trails 345 kV outage.
344566 | JEFFWOODY16_1 2 | -1 | MAYWOOD - ZACHARY 345 (5088) | RT | Peak | 2024-10-01 | 214.36 | 15 | 365.44 | 5481.53 | 14.9 | 4.08% | JEFF2 JEFFWOODY16_1 2 (LN/ALTW/ALTW) | Eastward wind transfer from South Central IA to Southeast IA and IL. Hills-Diamond Trail 345 kV outage. High wind generation. Excess MEC, ALTW generation.

## Oct-24 RT Off
cid | monitored | dir | ctg | mkt | class | moyr | std | cnt | avg | sum | per_avg | bind% | mon_name | drivers | notes
314718 | FORMAFORMN11_1 1 | 1 | HANKINSON-WAHPETON 230+WAHPETN TR2 | RT | Off-peak | 2024-10-01 | 168.9 | 163 | 295.78 | 48212.2 | 128.22 | 43.35% | FORMAN FORMAFORMN11_1 1 (LN/OTP/WAUE) | Summer ratings. Eastward wind transfer from MISO into SPP. Lisbon-Enderlin 69 kV outage. | Winter ratings from 11/1-4/1. Winter (only) B-ratings uprated from 131 MW to 169 MW in Winter 2024-25.
396264 | PRES_TIBB_1558 A | 1 | ASTER - COMMODORE 345 (4513) | RT | Off-peak | 2024-10-01 | 226.8 | 249 | 188.37 | 46904.01 | 124.74 | 66.22% | PRES PRES_TIBB_1558 A (LN/AMIL/AMIL) | Mt. Vernon-W. Frankfort 230 kV outage. Moderate sum of wind generation and coal generation. Load to the South, Southeast.
77127 | RAUNTEKAM16_1 1 | 1 | FORT CALHOUN-RAUN 345 | RT | Off-peak | 2024-10-01 | 253.97 | 136 | 268.06 | 36455.92 | 96.96 | 36.17% | RAUN RAUNTEKAM16_1 1 (LN/MEC/OPPD) | Southward wind transfer from the greater Sioux City, IA area (including SPP) into Omaha, NE. Flows show a strong negative correlation with Walter Scott Jr. output. | Curious B-rating uprate on 11/8/2024 from 217 MW to 284 MW. This was followed by a 1/30/2025 B-rating derate from 284 MW to 259 MW then again on 2/21/2025 from 259 MW to 256 MW and again on 4/7/2025 from 256 MW to 217 MW. Tekamah-Oakland 115 kV is a switching solution that relieves Tekamah-Substation 1226 at the expense of increasing flows on Raun-Tekamah.
455851 | PLESNLEEDS11_1 1 | 1 | BALTA GRE-RAMSEY 230 | RT | Off-peak | 2024-10-01 | 275.44 | 98 | 280.68 | 27506.58 | 73.16 | 26.07% | PLESNTLK PLESNLEEDS11_1 1 (LN/WAUE/WAUE) | Severe, unprecedented derate. Clean relationship between binding events and the derate. Hasn't bound since.
306800 | GRINNSGRIN69_1 1 | 1 | OTTUMWA - MONTEZUMA 345 | RT | Off-peak | 2024-10-01 | 562.35 | 34 | 674.82 | 22944.01 | 61.02 | 9.04% | GRINNEL GRINNSGRIN69_1 1 (LN/ALTW/ALTW) | Diamond Trail-Hills 345 kV, Powesheik Co-Reasnor 161 kV outages. Wind push.
350280 | OAHESULLY23_1 1 | 1 | LELAND OLDS - CHAPELLE CREEK 345 | RT | Off-peak | 2024-10-01 | 245.07 | 66 | 270.12 | 17827.75 | 47.41 | 17.55% | OAHE OAHESULLY23_1 1 (LN/WAUE/WAUE) | Ft. Thompson-Oahe Dam Ckt 2 230 kV outage (case outage -- no corresponding ticket!). Excess MDU load. Week MDU wind generation. Summer ratings.
465036 | RINGOL_SAILES3 A | -1 | LAYFIELD - CAROLL 230 | RT | Off-peak | 2024-10-01 | 773.3 | 15 | 952.64 | 14289.55 | 38 | 3.99% | RINGOL RINGOL_SAILES3 A (LN/EES/EES) | Sarepta-Longwood 345 kV outage. Weak Harrison County generation. Weak OK wind generation.
375350 | EXSPRNG_CARR A | 1 | OVERTON - SIBLEY - 3 345 | RT | Off-peak | 2024-10-01 | 473 | 24 | 561.49 | 13475.76 | 35.84 | 6.38% | MAUR_HS EXSPRNG_CARR A (LN/KCPL/KCPL) | Thomas Hill-Mead 161 kV outage. Heavy SPP wind generation. Thomas Hill outage.
344916 | 11303 A | -1 | FAIRPORT - GENTRY - NODAWAY 161 | RT | Off-peak | 2024-10-01 | 130.65 | 99 | 130.23 | 12892.92 | 34.29 | 26.33% | MIDWAY5 11303 A (LN/MPS/MPS) | White Cloud, Clear Creek, Rock Creek wind generation. Southwest IA wind generation. Excess load in St. Joseph, Kansas City.
72687 | 13831 A | 1 | BURNHAM-MUNSTER 345 (34504) | RT | Off-peak | 2024-10-01 | 220.4 | 59 | 209.61 | 12366.73 | 32.89 | 15.69% | CHICAGO 13831 A (LN/NIPS/NIPS) | Excess ComEd generation. Excess MEC generation. Sheffield-Gary Ave-Dune Acres 345 kV outages. Chicago Ave-Gary Ave 138 kV outage.
333296 | WOODYAPANO16_1 2 | 1 | HUGH - ZACHARY 345 | RT | Off-peak | 2024-10-01 | 245.12 | 39 | 291.05 | 11351 | 30.19 | 10.37% | WOODY WOODYAPANO16_1 2 (LN/ALTW/ALTW) | Southward wind transfer from IA into MO. Hills-Diamond Trails 345 kV outage.
462022 | MONROPRARC69_1 1 | -1 | OTTUMWA - MONTEZUMA 345 | RT | Off-peak | 2024-10-01 | 598.15 | 8 | 1374.83 | 10998.6 | 29.25 | 2.13% | MONROE5 MONROPRARC69_1 1 (LN/MEC/MEC) | Reasnor-Poweshiek Co-Irvine 161 kV outages. Hills-Diamond Trail 345 kV outage. Knoxville-Lucas 69 kV outages. Grinnell-S. Grinnell 69 kV outage.
349600 | WOODYAPANO16_1 2 | 1 | OTTUMWA - HUGH 345 | RT | Off-peak | 2024-10-01 | 238.24 | 34 | 295.15 | 10035.07 | 26.69 | 9.04% | WOODY WOODYAPANO16_1 2 (LN/ALTW/ALTW) | Southward wind transfer from IA into MO. Hills-Diamond Trails 345 kV outage. High wind generation. Low Ottumwa output.
349896 | ASTORIA TR11 | 1 | BROOKINGS COUNTY - ASTORIA 345 | RT | Off-peak | 2024-10-01 | 147.73 | 48 | 207.48 | 9958.88 | 26.49 | 12.77% | ASTORIA TR1 TR11 (XF/OTP/*) | Big Stone TR 230/115 kV, Big Stone-Brownsville 230 kV outages. High sensitivity to wind push at Dakota Range, Crowned Ridge, Deuel Harvest, etc. Clean relationship with Big Stone TR outage.
463281 | ALDRIMNPST_24 1 | 1 | HUBBARD - ERIE 230 | RT | Off-peak | 2024-10-01 | 362.11 | 22 | 434.3 | 9554.58 | 25.41 | 5.85% | ALDRICMP ALDRIMNPST_24 1 (LN/MP/MP) | Winger-Riverton, Hubbard-Audubon 230 kV outages. Wind generation to the West.
344566 | JEFFWOODY16_1 2 | -1 | MAYWOOD - ZACHARY 345 (5088) | RT | Off-peak | 2024-10-01 | 202.37 | 28 | 310.15 | 8684.26 | 23.1 | 7.45% | JEFF2 JEFFWOODY16_1 2 (LN/ALTW/ALTW) | Eastward wind transfer from South Central IA to Southeast IA and IL. Hills-Diamond Trail 345 kV outage. High wind generation. Excess MEC, ALTW generation.
302332 | HAZLTDUNDE16_1 1 | 1 | HAZLETON-HICKORY CREEK 345 | RT | Off-peak | 2024-10-01 | 129.16 | 47 | 164.07 | 7711.44 | 20.51 | 12.5% | HAZLTON HAZLTDUNDE16_1 1 (LN/ALTW/ALTW) | Clear relationship with Hazleton-Arnold 345 kV outage, which bottlenecks wind supply from IA and forces it over the constraint.
347564 | CRESTMARYV16_1 1 | -1 | NODAWAY - MARYVILLE 161 | RT | Off-peak | 2024-10-01 | 450.65 | 6 | 1165.67 | 6994.02 | 18.6 | 1.6% | CRESTON CRESTMARYV16_1 1 (LN/WAUE/AECI) | Maryville-Maryville 161 kV outage (extreme impact). Highly sensitive to Clear Creek, White Cloud wind push in the post-contingent setting with Maryville-Maryville 161 kV OOS.
416410 | MUDLAVERON13_1 1 | -1 | MUDLAKE - VERONA 138 2 | RT | Off-peak | 2024-10-01 | 237.13 | 32 | 208.66 | 6677.04 | 17.76 | 8.51% | MUDLAKE1 MUDLAVERON13_1 1 (LN/CONS/CONS) | Palisades-Argenta-Tompkins, Battle Ck-Oneida 345 kV outages. Verona-Convis 138 kV outage. | Will not bind when Calhoun Solar, Cereal City Solar are generating.
360096 | CHUB_LK TR1_2 | -1 | SCOTT CO - HELEN 345 | RT | Off-peak | 2024-10-01 | 263.94 | 27 | 243.11 | 6563.98 | 17.46 | 7.18% | CHUB_LK R1_2 TR1_2 (XF/NSP/*) | Wind transfer stepping down to 115 kV level. Clean relationship with Chub Lk-Hampton 345 kV outage. Excess MEC supply.